## Boiler overview
Figure. 1 The 12-MWth CFB boiler at Chalmers University of Technology
(1) combustion chamber; (2) fuel feed chute; (3) air plenum; (4) secondary air inlet at 2.1m; (5) secondary air inlet at 3.7m; (6) secondary air inlet at 5.4m;
(7) secondary air inlet into cyclone exit duct; (8) cyclone exit duct (9) hot primary cyclone; (10) particle return leg; (11) particle seal; (12) particle cooler;
(13) measurement hole cr1; (14) measurement hole cr2; (15) measurement hole after convection pass; (16) cold secondary cyclone; (17) bag house filter; lime bin;
(18) gas-extraction probe for emission monitoring; (19) flue gas fan; (20) sand bin; (21) lime bin; (22) hydrated lime bin;(23) fuel bunkers; (25) air fan;
(26) flue gas recirculation fan; (27) IACM instrument.
o
o
8
9
12
2
3
1
11
Rear
wall
Front
wall
4
5
10
5
4
6
6
7
7
16
17
19
21
20
23
23
25
18
22
23
26
24
13
14
Cycl. leg ash
sample
15
Deposit probe
27
Bed ash sample
bed removal
Fly ash1 sample
sec. cycl. ash removal
Fly ash2 sample
bag filter ash removal
Fuel 2
straw pellets
Fuel 1
wood chips
Emissions: NOx SO2, N2O, CO, hydrocarbons
Ack. ash
IACM

## Fuel 1 wood chips
Fuel bunker 1
Wood chips
Proximate analysis by mass: (as recieved); Fuel: wood chip 081022 kl 08:40+10:20+13:50
Combustibles= |  | 0.5815 | kg combustibles/kg fuel
Moisture= |  | 0.4159 | kg moisture/kg fuel
Ash= |  | 0.0026 | kg ash/kg fuel
Mass flow(wood chips)= |  | 1676.2069 | kg/h
Mass flow(wood chips)= |  | 979.0724 | kgDS/h | DS= Dry Substance
Mass flow (wood chips)= |  | 0.46561 | kg/s
Mass flow(wood chips)= |  | 974.7143 | kg combustibles/h
Ash flow in= |  | 4.3581 | kg/h
Ultimate analysis by mass: (moisture and ash free); SP wood chips F8 20878, 1 (blend sample 081022 08:40+10:20+13:50)
C= | 0.50201 | kg/kg combustibles
H= | 0.060241 | kg/kg combustibles
N= | 0.0013052 | kg/kg combustibles
S= | 0.0001004 | kg/kg combustibles
Cl= | 0.0001004 | kg/kg combustibles
O= | 0.43624 | kg/kg combustibles
Volatiles | 0.8143 | kg/kg combustibles
Heating value (low) |  | 18.6938 | MJ/kg combustibles
Ash analysis by mass; SP wood chips F8 20878, 1 (blend sample 081022 08:40+10:20+13:50). Ashed at 500°C
K= | 113 | g/kg ash
Na= | 6.4 | g/kg ash
Al= | 8.1 | g/kg ash
Si= | 33 | g/kg ash
Fe= | 17.7 | g/kg ash
Ca= | 213 | g/kg ash
Mg= | 34.7 | g/kg ash
P= | 17.9 | g/kg ash
Ti= | 0.7 | g/kg ash
Ba= | 2.7 | g/kg ash
Mn= | 13.9 | g/kg ash

## Fuel 2 straw pellets
Fuel bunker 3
Straw pellets
Proximate analysis by mass: (as recieved); Fuel: straw pellets 081022 kl 08:35+10:25+13:45
Combustibles= |  | 0.8363 | kg combustibles/kg fuel
Moisture= |  | 0.1312 | kg moisture/kg fuel
Ash= |  | 0.0325 | kg ash/kg fuel
Mass flow (straw)= |  | 314.588 | kg/h
Mass flow (straw)= |  | 273.314 | kgDS/h | DS= Dry Substance
Mass flow (straw)= |  | 0.087386 | kg/s
Mass flow (straw)= |  | 263.0899 | kg combustibles/h
Ash flow in= |  | 10.2241 | kg/h
Ultimate analysis by mass: (moisture and ash free); SP straw pellets F8 20878, 2 (blend sample 081022 08:35+10:25+13:45).
C= | 0.49376 | kg/kg combustibles
H= | 0.06237 | kg/kg combustibles
N= | 0.0090437 | kg/kg combustibles
S= | 0.0010395 | kg/kg combustibles
Cl= | 0.0018711 | kg/kg combustibles
O= | 0.43191 | kg/kg combustibles
Volatiles | 0.8027 | kg/kg combustibles
Heating value (low) |  | 18.4501 | MJ/kg combustibles
Ash analysis by mass, SP straw pellets F8 20878, 2 (blend sample 081022 08:35+10:25+13:45). Ashed at 500°C
K= | 151 | g/kg ash
Na= | 7.9 | g/kg ash
Al= | 8.4 | g/kg ash
Si= | 201 | g/kg ash
Fe= | 6 | g/kg ash
Ca= | 68.5 | g/kg ash
Mg= | 28 | g/kg ash
P= | 23.3 | g/kg ash
Ti= | 0.5 | g/kg ash
Ba= | 1 | g/kg ash
Mn= | 1 | g/kg ash

## Flyash1
Flyash 1: Secondary cyclone ash
Flow: | 4.8186 | kg ash (inert)/h
Ash analysis by mass; SP F8 20878 no 6
K= | 32.1641 | g/kg ash
Na= | 4.6411 | g/kg ash
Al= | 13.9234 | g/kg ash
Si= | 154.3443 | g/kg ash
Fe= | 38.2083 | g/kg ash
Ca= | 137.075 | g/kg ash
Mg= | 14.571 | g/kg ash
P= | 9.714 | g/kg ash
Ti= | 1.4031 | g/kg ash
Ba= | 1.1873 | g/kg ash
Mn= | 6.7998 | g/kg ash
S= | 17.2693 | g/kg ash
Cl= | 11.8726 | g/kg ash
Ash analysis= |  | 0.9265 | kg ash/kg ash+combusibles

## Flyash2
Flyash 2: Bag filter ash
Flow: | 2.7126 | kg ash (inert)/h
Ash analysis by mass; SP F8 20878 no 8
K= | 18.8539 | g/kg ash
Na= | 5.402 | g/kg ash
Al= | 24.7855 | g/kg ash
Si= | 64.8236 | g/kg ash
Fe= | 122.8683 | g/kg ash
Ca= | 197.013 | g/kg ash
Mg= | 23.5145 | g/kg ash
P= | 13.8756 | g/kg ash
Ti= | 4.5546 | g/kg ash
Ba= | 3.1776 | g/kg ash
Mn= | 12.075 | g/kg ash
S= | 22.2434 | g/kg ash
Cl= | 33.8947 | g/kg ash
Ash analysis= |  | 0.9441 | kg ash/kg ash+combusibles

## Bottom bed ash
Bottom bed ash:
Flow: | 0 | kg ash (inert)/h
Ash analysis by mass; SP F8 20878 no 4
K= | 11.8355 | g/kg ash
Na= | 1.8054 | g/kg ash
Al= | 3.1093 | g/kg ash
Si= | 427.2818 | g/kg ash
Fe= | 1.9057 | g/kg ash
Ca= | 18.0542 | g/kg ash
Mg= | 3.9117 | g/kg ash
P= | 2.1063 | g/kg ash
Ti= | 0.5015 | g/kg ash
Ba= | 0.4012 | g/kg ash
Mn= | 2.006 | g/kg ash
S= | 0.2006 | g/kg ash
Cl= | 0.1003 | g/kg ash
Ash analysis= |  | 0.997 | kg ash/kg ash+combusibles

## Cyclone leg ash
Cyclone leg ash:
Flow: | 0 | kg/h
Cyclone leg sample 2008-10-21 at 16:00; No analysis performed on this sample

## Ack. ash in conv. pass
Ackumulated ash in the convection section of the boiler
Flow: | 7.051 | kg ash (inert)/h |  | (the amount of ash ackumulted in the convection section is recalculated as an ash flow)
Ash analysis by mass; SP F8 20878 no 6 (The ackumulated ash in the convection section has the same composition as collected secondary cyclone ash)
K= | 32.1641 | g/kg ash
Na= | 4.6411 | g/kg ash
Al= | 13.9234 | g/kg ash
Si= | 154.3443 | g/kg ash
Fe= | 38.2083 | g/kg ash
Ca= | 137.075 | g/kg ash
Mg= | 14.571 | g/kg ash
P= | 9.714 | g/kg ash
Ti= | 1.4031 | g/kg ash
Ba= | 1.1873 | g/kg ash
Mn= | 6.7998 | g/kg ash
S= | 17.2693 | g/kg ash
Cl= | 11.8726 | g/kg ash
Ash analysis= |  | 0.9265 | kg ash/kg ash+combusibles

## Specie balances
Specie